## Instructions
Tool version 2.0
2026-04-29
Cellar Cooling SEPR Calculation Tool - Instructions
About this calculation tool
This calculation tool is provided to help suppliers to calculate the Seasonal Energy Performance Ratio (SEPR) for their products based upon 4 rating point measurements (or calculations) of COP.
It is intended to assist suppliers to assess the seasonal performance of their products according to a methodology that is to be used under the ETL
This tool is provided free of charge and in good faith but without guarantee of accuracy. Users should satisfy themselves that the output meets the requirement in the document: ETL Cellar Cooling equipment in conjunction with BS EN 14825:2022 which explains more details of the methodology.
Temperature References (°C):
What is SEPR? Seasonal Energy Performance Ratio |  |  | A | B | C | D
SEPR is the seasonal energy performance ratio of a condensing unit. It is calculated from the COP of the condensing unit at 4 different ambient temperatures (see table) and cooling loads, called rating points. The required rating points are specified in the document 'SEPR calculation method', showing for each rating point the necessary part load ratio and air dry bulb temperature for the outdoor heat exchanger. Ambient temperature references see table. | External air |  | 32 | 25 | 15 | 5
| Internal Air | Tdb | 10 | 10 | 10 | 10
How to use the tool |  | Hum % | 80 | 80 | 80 | 80
There are two sheets: One for fixed capacity and stepless condensing units and a second for stepped capacity condensing (Inverter) units. Use the one appropriate to the condensing unit.
To use the spreadsheet, please insert the full load rated capacity in cell D3, and then declared rated capacity at the 3 part load rating points (B, C and D - cells D9:11) as well as the declared COP at 4 rating points (cells E8:11). In case of step capacity control also insert part load DC and COP at 3 rating points (B, C, D - cells F9:G11) The spreadsheet then calculates the required SEPR automatically using a linear interpolation between the rating points A, B, C, and D and an assumption of a constant capacity for temperatures above A and below D.
Feedback
Feedback will be used to help improve the tool.
If you have any questions or comments about the use of this tool please send an email to:
info@etl.energysecurity.gov.uk
Please put the phrase 'Cellar Cooler Calculation Tool' in the subject line.

## Cellar Cooler - Fixed Capacity
Condensing Unit (MT) − Fix Capacity or Stepless Capacity Control | [6 empty] | Tool version 2.0 | 2026-04-29
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 5.43
[6 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) |  |  |  | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 2.46 | 5.43 | 5.43 | 2.46 | 0.25 | 1 | 2.46 |  | Use default for Cd or measured value if verified by test
COP B | 2.88 | 4.5356 | 5.65 | 2.88 | 0.25 | 0.80277 | 2.738
COP C | 2.88 | 3.258 | 5.65 | 2.88 | 0.25 | 0.57664 | 2.5752 |  | For frther information see
COP D | 2.88 | 3.258 | 5.65 | 2.88 | 0.25 | 0.57664 | 2.5752 |  | "Instructions" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC | COP at part load for fix capacity units: Calculation following
| 1 | -19 | 0.083351 | 60% | 3.258 | 2.5752 | 0.27156 | 0.10545 | the principle of EN 14825
| 2 | -18 | 0.40727 | 60% | 3.258 | 2.5752 | 1.3269 | 0.51526
| 3 | -17 | 0.64624 | 60% | 3.258 | 2.5752 | 2.1055 | 0.8176
| 4 | -16 | 1.0535 | 60% | 3.258 | 2.5752 | 3.4324 | 1.3329
| 5 | -15 | 1.7412 | 60% | 3.258 | 2.5752 | 5.6728 | 2.2029
| 6 | -14 | 2.9786 | 60% | 3.258 | 2.5752 | 9.7043 | 3.7684
| 7 | -13 | 3.793 | 60% | 3.258 | 2.5752 | 12.3576 | 4.7987
| 8 | -12 | 5.6854 | 60% | 3.258 | 2.5752 | 18.5231 | 7.1929 | Degradation Coefficient (Cd) at part load for fix capacity units:
| 9 | -11 | 8.937 | 60% | 3.258 | 2.5752 | 29.1168 | 11.3067 | Since condensing units are no functional system Cd can not be determined by test.
| 10 | -10 | 11.8115 | 60% | 3.258 | 2.5752 | 38.4818 | 14.9434 | For this case the default degradation coefficient Cd shall be 0.25 − following the
| 11 | -9 | 17.2861 | 60% | 3.258 | 2.5752 | 56.3181 | 21.8696 | principle of EN 14825.
| 12 | -8 | 20.0184 | 60% | 3.258 | 2.5752 | 65.2201 | 25.3264
| 13 | -7 | 28.7314 | 60% | 3.258 | 2.5752 | 93.6068 | 36.3496
| 14 | -6 | 39.7062 | 60% | 3.258 | 2.5752 | 129.3627 | 50.2344
| 15 | -5 | 56.6131 | 60% | 3.258 | 2.5752 | 184.4454 | 71.6243
| 16 | -4 | 76.3625 | 60% | 3.258 | 2.5752 | 248.789 | 96.6104
| 17 | -3 | 106.0655 | 60% | 3.258 | 2.5752 | 345.5615 | 134.1893
| 18 | -2 | 153.222 | 60% | 3.258 | 2.5752 | 499.1973 | 193.8496
| 19 | -1 | 203.4136 | 60% | 3.258 | 2.5752 | 662.7215 | 257.3497
| 20 | 0 | 247.9751 | 60% | 3.258 | 2.5752 | 807.9029 | 313.7269
| 21 | 1 | 282.0066 | 60% | 3.258 | 2.5752 | 918.7775 | 356.782
| 22 | 2 | 275.9131 | 60% | 3.258 | 2.5752 | 898.9249 | 349.0728
| 23 | 3 | 300.6113 | 60% | 3.258 | 2.5752 | 979.3915 | 380.3198
| 24 | 4 | 310.7673 | 60% | 3.258 | 2.5752 | 1012.4799 | 393.1688
D | 25 | 5 | 336.4773 | 60% | 3.258 | 2.5752 | 1096.2432 | 425.696
| 26 | 6 | 350.4772 | 60% | 3.258 | 2.5752 | 1141.8548 | 443.408
| 27 | 7 | 363.4945 | 60% | 3.258 | 2.5752 | 1184.265 | 459.8768
| 28 | 8 | 368.9063 | 60% | 3.258 | 2.5752 | 1201.8967 | 466.7236
| 29 | 9 | 371.6343 | 60% | 3.258 | 2.5752 | 1210.7847 | 470.175
| 30 | 10 | 377.3222 | 60% | 3.258 | 2.5752 | 1229.3156 | 477.371
| 31 | 11 | 376.5281 | 60% | 3.258 | 2.5752 | 1226.7284 | 476.3663
| 32 | 12 | 386.4212 | 60% | 3.258 | 2.5752 | 1258.9602 | 488.8826
| 33 | 13 | 389.843 | 60% | 3.258 | 2.5752 | 1270.1085 | 493.2118
| 34 | 14 | 384.448 | 60% | 3.258 | 2.5752 | 1252.5315 | 486.3862
C | 35 | 15 | 370.4541 | 60% | 3.258 | 2.5752 | 1206.9396 | 468.6819
| 36 | 16 | 344.9639 | 62.35% | 3.3858 | 2.5915 | 1167.9665 | 450.6982
| 37 | 17 | 328.0247 | 64.71% | 3.5135 | 2.6077 | 1152.5246 | 441.9627
| 38 | 18 | 305.3627 | 67.06% | 3.6413 | 2.624 | 1111.9153 | 423.7444
| 39 | 19 | 261.8688 | 69.41% | 3.7691 | 2.6403 | 986.9989 | 373.82
| 40 | 20 | 223.8986 | 71.76% | 3.8968 | 2.6566 | 872.4934 | 328.4265
| 41 | 21 | 196.3056 | 74.12% | 4.0246 | 2.6729 | 790.0493 | 295.5811
| 42 | 22 | 163.0446 | 76.47% | 4.1524 | 2.6891 | 677.0186 | 251.7594
| 43 | 23 | 141.7763 | 78.82% | 4.2801 | 2.7054 | 606.8194 | 224.2968
| 44 | 24 | 121.9296 | 81.18% | 4.4079 | 2.7217 | 537.4512 | 197.468
B | 45 | 25 | 104.4601 | 83.53% | 4.5356 | 2.738 | 473.7941 | 173.0443
| 46 | 26 | 85.7688 | 85.88% | 4.6634 | 2.6983 | 399.9752 | 148.2334
| 47 | 27 | 71.5382 | 88.24% | 4.7912 | 2.6586 | 342.7521 | 128.9236
| 48 | 28 | 56.5744 | 90.59% | 4.9189 | 2.6189 | 278.2861 | 106.2625
| 49 | 29 | 43.3482 | 92.94% | 5.0467 | 2.5791 | 218.7654 | 84.8211
| 50 | 30 | 31.024 | 95.29% | 5.1745 | 2.5394 | 160.5329 | 63.2162
| 51 | 31 | 20.2062 | 97.65% | 5.3022 | 2.4997 | 107.1378 | 42.86
A | 52 | 32 | 11.8503 | 100% | 5.43 | 2.46 | 64.3473 | 26.1574
| 53 | 33 | 8.1679 | 100% | 5.43 | 2.46 | 44.3515 | 18.0291
| 54 | 34 | 3.8297 | 100% | 5.43 | 2.46 | 20.795 | 8.4533
| 55 | 35 | 2.0914 | 100% | 5.43 | 2.46 | 11.3561 | 4.6163
| 56 | 36 | 1.2076 | 100% | 5.43 | 2.46 | 6.557 | 2.6655
| 57 | 37 | 0.5218 | 100% | 5.43 | 2.46 | 2.8334 | 1.1518
| 58 | 38 | 0.40138 | 100% | 5.43 | 2.46 | 2.1795 | 0.88598
[6 empty] | total | 30340.2203 | 11681.3146
[7 empty] | SEPR | 2.5973
Note on E8: COP A related to: 32°C ambient temperature -10°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -10°C evaporating temperature
DC = declared cooling capacity at temperatures A, B, C and D
Please consider: Selection of COPA, COPB & COPC depends on different ambient temp conditions, load profile. Application temperature =10.0°C db +/- 5% & 80% Humidity +/-5%
Ratio between cooling demand and declared capacity (CR=1, in case of a continuous capacity adjustment)
DC at rating points B, C and D shall not be lower than 97%
of the cooling demand (PR) -- CR < 1.03
COP
COP

## Cellar Cooler - Inverter
Condensing Unit (MT) − Step Capacity Control | [6 empty] | Tool version 2.0 | 2026-04-29
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 7
[8 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | DC at part load (measured or calculated) | COP at part load (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) | [5 empty] | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 2.1 | 7 | 7 | 2.1 | − | − | 0.25 | 1 | 2.1 |  | Use default for Cd or measured value if verified by test and not to be changed
COP B | 2.57 | 5.8471 | 7.76 | 2.57 | 3.1 | 2.44 | 0.25 | 0.75349 | 2.5166
COP C | 3.27 | 4.2 | 8.74 | 3.27 | 3.5 | 3.1 | 0.25 | 0.48055 | 3.1227 |  | For further information see
COP D | 4 | 4.2 | 9.61 | 4 | 3.84 | 3.8 | 0.25 | 0.43704 | 3.8125 |  | "Instructions" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC
| 1 | -19 | 0.083351 | 60% | 4.2 | 3.8125 | 0.35008 | 0.091824
| 2 | -18 | 0.40727 | 60% | 4.2 | 3.8125 | 1.7105 | 0.44867
| 3 | -17 | 0.64624 | 60% | 4.2 | 3.8125 | 2.7142 | 0.71193
| 4 | -16 | 1.0535 | 60% | 4.2 | 3.8125 | 4.4248 | 1.1606 |  | COP at part load in case DC at part load is higher than cooling demand:
| 5 | -15 | 1.7412 | 60% | 4.2 | 3.8125 | 7.313 | 1.9182 |  | Calculation following the principle of EN 14825
| 6 | -14 | 2.9786 | 60% | 4.2 | 3.8125 | 12.5101 | 3.2814
| 7 | -13 | 3.793 | 60% | 4.2 | 3.8125 | 15.9306 | 4.1785
| 8 | -12 | 5.6854 | 60% | 4.2 | 3.8125 | 23.8787 | 6.2633
| 9 | -11 | 8.937 | 60% | 4.2 | 3.8125 | 37.5355 | 9.8454
| 10 | -10 | 11.8115 | 60% | 4.2 | 3.8125 | 49.6083 | 13.0121
| 11 | -9 | 17.2861 | 60% | 4.2 | 3.8125 | 72.6017 | 19.0432
| 12 | -8 | 20.0184 | 60% | 4.2 | 3.8125 | 84.0774 | 22.0532 |  | Degradation Coefficient (Cd) at part load for fix capacity units:
| 13 | -7 | 28.7314 | 60% | 4.2 | 3.8125 | 120.6717 | 31.6518 |  | Since condensing units are no functional system Cd can not be determined by test.
| 14 | -6 | 39.7062 | 60% | 4.2 | 3.8125 | 166.7658 | 43.7421 |  | For this case the default degradation coefficient Cd shall be 0.25 − following the
| 15 | -5 | 56.6131 | 60% | 4.2 | 3.8125 | 237.7749 | 62.3675 |  | principle of EN 14825
| 16 | -4 | 76.3625 | 60% | 4.2 | 3.8125 | 320.7224 | 84.1244
| 17 | -3 | 106.0655 | 60% | 4.2 | 3.8125 | 445.4753 | 116.8466
| 18 | -2 | 153.222 | 60% | 4.2 | 3.8125 | 643.5325 | 168.7964
| 19 | -1 | 203.4136 | 60% | 4.2 | 3.8125 | 854.3371 | 224.0897
| 20 | 0 | 247.9751 | 60% | 4.2 | 3.8125 | 1041.4954 | 273.1807
| 21 | 1 | 282.0066 | 60% | 4.2 | 3.8125 | 1184.4277 | 310.6713
| 22 | 2 | 275.9131 | 60% | 4.2 | 3.8125 | 1158.8351 | 303.9585
| 23 | 3 | 300.6113 | 60% | 4.2 | 3.8125 | 1262.5673 | 331.1671
| 24 | 4 | 310.7673 | 60% | 4.2 | 3.8125 | 1305.2227 | 342.3554
D | 25 | 5 | 336.4773 | 60% | 4.2 | 3.8125 | 1413.2049 | 370.6788
| 26 | 6 | 350.4772 | 60% | 4.2 | 3.7435 | 1472.0043 | 393.2159
| 27 | 7 | 363.4945 | 60% | 4.2 | 3.6745 | 1526.6768 | 415.476
| 28 | 8 | 368.9063 | 60% | 4.2 | 3.6055 | 1549.4064 | 429.7284
| 29 | 9 | 371.6343 | 60% | 4.2 | 3.5366 | 1560.8642 | 441.3496
| 30 | 10 | 377.3222 | 60% | 4.2 | 3.4676 | 1584.7531 | 457.018
| 31 | 11 | 376.5281 | 60% | 4.2 | 3.3986 | 1581.4179 | 465.3121
| 32 | 12 | 386.4212 | 60% | 4.2 | 3.3296 | 1622.9689 | 487.4307
| 33 | 13 | 389.843 | 60% | 4.2 | 3.2607 | 1637.3406 | 502.1495
| 34 | 14 | 384.448 | 60% | 4.2 | 3.1917 | 1614.6815 | 505.9023
C | 35 | 15 | 370.4541 | 60% | 4.2 | 3.1227 | 1555.9074 | 498.2555
| 36 | 16 | 344.9639 | 62.35% | 4.3647 | 3.0621 | 1505.6658 | 491.7098
| 37 | 17 | 328.0247 | 64.71% | 4.5294 | 3.0015 | 1485.7591 | 495.0064
| 38 | 18 | 305.3627 | 67.06% | 4.6941 | 2.9409 | 1433.4083 | 487.4067
| 39 | 19 | 261.8688 | 69.41% | 4.8588 | 2.8803 | 1272.3742 | 441.7537
| 40 | 20 | 223.8986 | 71.76% | 5.0235 | 2.8197 | 1124.7613 | 398.8979
| 41 | 21 | 196.3056 | 74.12% | 5.1882 | 2.7591 | 1018.4798 | 369.1395
| 42 | 22 | 163.0446 | 76.47% | 5.3529 | 2.6985 | 872.768 | 323.4322
| 43 | 23 | 141.7763 | 78.82% | 5.5176 | 2.6378 | 782.2718 | 296.5566
| 44 | 24 | 121.9296 | 81.18% | 5.6824 | 2.5772 | 692.8469 | 268.8327
B | 45 | 25 | 104.4601 | 83.53% | 5.8471 | 2.5166 | 610.7844 | 242.6989
| 46 | 26 | 85.7688 | 85.88% | 6.0118 | 2.4571 | 515.6218 | 209.8484
| 47 | 27 | 71.5382 | 88.24% | 6.1765 | 2.3976 | 441.8535 | 184.2902
| 48 | 28 | 56.5744 | 90.59% | 6.3412 | 2.3381 | 358.7482 | 153.4373
| 49 | 29 | 43.3482 | 92.94% | 6.5059 | 2.2786 | 282.018 | 123.7704
| 50 | 30 | 31.024 | 95.29% | 6.6706 | 2.219 | 206.9485 | 93.2604
| 51 | 31 | 20.2062 | 97.65% | 6.8353 | 2.1595 | 138.115 | 63.9564
A | 52 | 32 | 11.8503 | 100% | 7 | 2.1 | 82.9523 | 39.5011
| 53 | 33 | 8.1679 | 100% | 7 | 2.1 | 57.1751 | 27.2262
| 54 | 34 | 3.8297 | 100% | 7 | 2.1 | 26.8076 | 12.7655
| 55 | 35 | 2.0914 | 100% | 7 | 2.1 | 14.6395 | 6.9712
| 56 | 36 | 1.2076 | 100% | 7 | 2.1 | 8.4529 | 4.0252
| 57 | 37 | 0.5218 | 100% | 7 | 2.1 | 3.6526 | 1.7393
| 58 | 38 | 0.40138 | 100% | 7 | 2.1 | 2.8097 | 1.3379
[6 empty] | total | 39112.6228 | 12079.0406
[7 empty] | SEPR | 3.2381
DC = declared cooling capacity at temperatures A, B, C and D
Please consider: Selection of COPA, COPB & COPC depends on different ambient temp conditions, load profile. Application temperature =10.0°C db +/- 5% & 80% Humidity +/-5%
Ratio between cooling demand and declared capacity (CR=1, in case of a continuous capacity adjustment)
Measured or calculated cooling capacity equal or above cooling demand
Measured or calculated part load capacity below cooling demand. Leave DC and COP blank if step control not available/necessary. Lowest part load DC limited to > 10% of DC at full load.
For step control, COP is a linear interpolation between the operating points above and below cooling demand
COP
COP
Note on E8: COP A related to: 32°C ambient temperature -10°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on F9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on G9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on F10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on G10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -10°C evaporating temperature
Note on F11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on G11: COP D related to: 5°C ambient temperature -10°C evaporating temperature